## model_setup
wildcard | simulation_years | existing_eskom | existing_non_eskom | new_build_limits | projected_parameters | costs
val-LC-UNC | 2020,2022,2024,2026,2028,2030,2032,2034,2036,2038,2040,2042,2044,2046,2048,2050 | LC-Retirement | base | base | ambitions | ambitions_2019
val-LC-UNC-1 | 2020,2022,2024,2026,2028,2030,2032,2034,2036,2038,2040,2042,2044,2046,2048,2050 | LC-Retirement | base | base | ambitions | ambitions_2019
val-LC-UNC-2 | 2020,2025,2030,2035,2040,2045,2050 | LC-Retirement | base | base | ambitions | ambitions_2019
val-2Gt-UNC | 2020,2022,2024,2026,2028,2030,2032,2034,2036,2038,2040,2042,2044,2046,2048,2050 | 2Gt-Retirement | base | base | ambitions | ambitions_2019
val-2Gt-UNC-1 | 2020,2021,2022,2023,2024,2025,2026,2027,2028,2029,2030,2031,2032,2033,2034,2035,2036,2037,2038,2039,2040,2045,2050 | 2Gt-Retirement | base | base | ambitions | ambitions_2019
val-2Gt-UNC-2 | 2020,2025,2030,2035,2040,2045,2050 | 2Gt-Retirement | base | base | ambitions | ambitions_2019
val-LC-SMOOTH | 2020,2022,2024,2026,2028,2030,2032,2034,2036,2038,2040,2042,2044,2046,2048,2050 | base | base | ambitions_LC_SMOOTH | ambitions | ambitions_2019
val-LC-SMOOTH-1 | 2020,2022,2024,2026,2028,2030,2032,2034,2036,2038,2040,2042,2044,2046,2048,2050 | LC-Retirement | base | ambitions_LC_SMOOTH | ambitions | ambitions_2019
val-LC-SMOOTH-2 | 2020,2025,2030,2035,2040,2045,2050 | LC-Retirement | base | ambitions_LC_SMOOTH | ambitions | ambitions_2019
val-2Gt-SMOOTH | 2020,2022,2024,2026,2028,2030,2032,2034,2036,2038,2040,2042,2044,2046,2048,2050 | 2Gt | base | ambitions_2Gt_SMOOTH | ambitions | ambitions_2019
val-2Gt-SMOOTH-1 | 2020,2022,2024,2026,2028,2030,2032,2034,2036,2038,2040,2042,2044,2046,2048,2050 | LC-Retirement | base | ambitions_2Gt_SMOOTH | ambitions | ambitions_2019

## existing_eskom
Scenario | Power Station Name | Carrier | Type | Status | Capacity (MW) | Unit size (MW) | Number units | Future Commissioning Date | Decommissioning Date | Heat Rate (GJ/MWh) | Fuel Price (R/GJ) | Max Ramp Up (MW/min) | Max Ramp Down (MW/min) | Min Stable Level (%) | Variable O&M Cost (R/MWh) | Fixed O&M Cost (R/kW/yr) | Pump Efficiency (%) | Pump Units | Pump Load per unit (MW) | Pumped Storage - Max Storage (GWh) | CSP Storage (hours) | Diesel Storage (Ml) | Gas storage (MCM) | GPS Latitude | GPS Longitude
base | Arnot* | coal | Generator | Existing | 1116 | 372 | 3 | - | 2027 | 12.744 | 25.9 | 2.1 | 2.1 | 30% | 98 | 1133 | - | - | - | - | - |  |  | -25.9444 | 29.7917
base | Arnot** | coal | Generator | Existing | 1116 | 372 | 3 | - | 2030 | 12.744 | 25.9 | 2.1 | 2.1 | 30% | 98 | 1133 | - | - | - | - | - | 0 | 0 | -25.9444 | 29.7917
base | Camden* | coal | Generator | Existing | 740 | 370 | 2 | - | 2022 | 13.584 | 32.3 | 1.1 | 1.1 | 30% | 98 | 1133 | - | - | - | - | - |  |  | -26.6201 | 30.0911
base | Camden** | coal | Generator | Existing | 370 | 370 | 1 | - | 2024 | 14.28 | 32.3 | 1.1 | 1.1 | 30% | 98 | 1133 | - | - | - | - | - |  |  | -26.6201 | 30.0911
base | Duvha* | coal | Generator | Existing | 1150 | 575 | 2 | - | 2032 | 12.066 | 18 | 3.3 | 3.3 | 30% | 98 | 1133 | - | - | - | - | - |  |  | -25.9595 | 29.3409
base | Duvha** | coal | Generator | Existing | 1725 | 575 | 3 |  | 2035 | 12.066 | 18 | 3.3 | 3.3 | 30% | 98 | 1133 | - | - | - | - | - | 0 | 0 | -25.9595 | 29.3409
base | Grootvlei* | coal | Generator | Existing | 286 | 143 | 2 | - | 2019 | 13.79 | 29.8 | 0.9 | 0.9 | 30% | 98 | 1133 | - | - | - | - | - |  |  | -26.7695 | 28.4995
base | Grootvlei** | coal | Generator | Existing | 286 | 143 | 2 |  | 2020 | 13.79 | 29.8 | 0.9 | 0.9 | 30% | 98 | 1133 | - | - | - | - | - | 0 | 0 | -26.7695 | 28.4995
base | Hendrina* | coal | Generator | Existing | 440 | 110 | 4 | - | 2021 | 13.266 | 28.7 | 1.1 | 1.1 | 30% | 98 | 1133 | - | - | - | - | - |  |  | -26.0314 | 29.6014
base | Hendrina** | coal | Generator | Existing | 440 | 110 | 4 |  | 2023 | 13.266 | 28.7 | 1.1 | 1.1 | 30% | 98 | 1133 | - | - | - | - | - | 0 | 0 | -26.0314 | 29.6014
base | Kendal* | coal | Generator | Existing | 1920 | 640 | 3 | - | 2041 | 11.782 | 24.3 | 1.8 | 1.8 | 30% | 98 | 1133 | - | - | - | - | - |  |  | -26.088 | 28.9689
base | Kendal** | coal | Generator | Existing | 1920 | 640 | 3 |  | 2044 | 11.782 | 24.3 | 1.8 | 1.8 | 30% | 98 | 1133 | - | - | - | - | - | 0 | 0 | -26.088 | 28.9689
base | Komati | coal | Generator | Existing | 114 | 114 | 1 | - | 2022 | 15.123 | 34.7 | 0.5 | 0.5 | 30% | 98 | 1133 | - | - | - | - | - |  |  | -26.0908 | 29.4745
base | Kriel* | coal | Generator | Existing | 1425 | 475 | 3 | - | 2024 | 12.995 | 28.6 | 3.6 | 3.6 | 30% | 98 | 1133 | - | - | - | - | - |  |  | -26.254 | 29.1801
base | Kriel** | coal | Generator | Existing | 1425 | 475 | 3 |  | 2028 | 12.995 | 28.6 | 3.6 | 3.6 | 30% | 98 | 1133 | - | - | - | - | - | 0 | 0 | -26.254 | 29.1801
base | Kusile* | coal | Generator | Existing | 2880 | 720 | 4 | - | beyond 2050 | 10.305 | 31.6 | 7.2 | 7.2 | 30% | 98 | 1133 | - | - | - | - | - |  |  | -25.5459 | 28.5502
base | Kusile** | coal | Generator | Existing | 720 | 720 | 1 | 2023 | beyond 2050 | 10.305 | 31.6 | 7.2 | 7.2 | 30% | 98 | 1133 | - | - | - | - | - | 0 | 0 | -25.5459 | 28.5502
base | Kusile*** | coal | Generator | Existing | 720 | 720 | 1 | 2024 | beyond 2050 | 10.305 | 31.6 | 7.2 | 7.2 | 30% | 98 | 1133 | - | - | - | - | - | 0 | 0 | -25.5459 | 28.5502
base | Lethabo* | coal | Generator | Existing | 1779 | 593 | 3 | - | 2039 | 11.003 | 14.4 | 5.9 | 5.9 | 30% | 98 | 1133 | - | - | - | - | - |  |  | -26.7403 | 27.975
base | Lethabo** | coal | Generator | Existing | 1779 | 593 | 3 |  | 2042 | 11.003 | 14.4 | 5.9 | 5.9 | 30% | 98 | 1133 | - | - | - | - | - | 0 | 0 | -26.7403 | 27.975
base | Majuba* | coal | Generator | Existing | 1833 | 611 | 3 | - | 2031 | 11.782 | 32.1 | 1.7 | 1.7 | 30% | 98 | 1133 | - | - | - | - | - |  |  | -27.0955 | 29.7706
base | Majuba** | coal | Generator | Existing | 2010 | 670 | 3 | - | 2050 | 11.032 | 32.1 | 1.9 | 1.9 | 30% | 98 | 1133 | - | - | - | - | - |  |  | -27.0955 | 29.7706
base | Matimba* | coal | Generator | Existing | 1845 | 615 | 3 | - | 2040 | 11.682 | 17.5 | 3 | 3 | 30% | 98 | 1133 | - | - | - | - | - |  |  | -23.6678 | 27.6128
base | Matimba** | coal | Generator | Existing | 1845 | 615 | 3 |  | 2043 | 11.682 | 17.5 | 3 | 3 | 30% | 98 | 1133 | - | - | - | - | - | 0 | 0 | -23.6678 | 27.6128
base | Matla* | coal | Generator | Existing | 1725 | 575 | 3 | - | 2032 | 12.066 | 30.2 | 2.4 | 2.4 | 30% | 98 | 1133 | - | - | - | - | - |  |  | -26.2804 | 29.1423
base | Matla** | coal | Generator | Existing | 1725 | 575 | 3 |  | 2034 | 12.066 | 30.2 | 2.4 | 2.4 | 30% | 98 | 1133 | - | - | - | - | - | 0 | 0 | -26.2804 | 29.1423
base | Medupi* | coal | Generator | Existing | 3615 | 723 | 5 | - | beyond 2050 | 10.305 | 21.4 | 7.2 | 7.2 | 30% | 98 | 1133 | - | - | - | - | - |  |  | -23.42 | 27.33
base | Medupi** | coal | Generator | Existing | 723 | 723 | 1 |  | beyond 2050 | 10.305 | 21.4 | 7.2 | 7.2 | 30% | 98 | 1133 | - | - | - | - | - | 0 | 0 | -23.42 | 27.33
base | Tutuka* | coal | Generator | Existing | 1755 | 585 | 3 | - | 2040 | 10.495 | 32.3 | 3.2 | 3.2 | 30% | 98 | 1133 | - | - | - | - | - |  |  | -26.7756 | 29.3521
base | Tutuka** | coal | Generator | Existing | 1755 | 585 | 3 |  | 2042 | 10.495 | 32.3 | 3.2 | 3.2 | 30% | 98 | 1133 | - | - | - | - | - | 0 | 0 | -26.7756 | 29.3521
base | Sere | onwind | Generator | Existing | 100 | 2 | 50 | - | 2034 | - | - | - | - | 30% | 737 | 0 | - | - | - | - | - |  |  | -31.5018 | 18.1143
base | Koeberg | nuclear | Generator | Existing | 1854 | 930 | 2 | - | 2047 | 11.111 | 8.5 | - | - | 30% | 45 | 1187 | - | - | - | - | - |  |  | -33.6737 | 18.4281
base | Drakensberg | PHS | StorageUnit | Existing | 1000 | 250 | 4 | - | beyond 2050 | - | - | - | - | 30% | 0.0001 | 222 | 73.7% | 4 | 250 | 21.7 | - |  |  | -28.5628 | 29.0828
base | Ingula | PHS | StorageUnit | Existing | 1332 | 333 | 4 | - | beyond 2050 | - | - | - | - | 30% | 0.0002 | 2796 | 78% | 4 | 333 | 27.4 | - |  |  | -28.165 | 29.3512
base | Palmiet | PHS | StorageUnit | Existing | 400 | 200 | 2 | - | beyond 2050 | - | - | - | - | 30% | 0.0003 | 222 | 77.9% | 2 | 200 | 10 | - |  |  | -34.1972 | 18.9736
base | Gariep | hydro | Generator | Existing | 360 | 90 | 4 | - | beyond 2050 | - | - | - | - | 30% | 350 | 0 | - | - | - | - | - |  |  | -30.624 | 25.504
base | Vanderkloof | hydro | Generator | Existing | 240 | 120 | 2 | - | beyond 2050 | - | - | - | - | 30% | 350 | 0 | - | - | - | - | - |  |  | -29.9934 | 24.7338
base | Acacia | gas | Generator | Existing | 171 | 57 | 3 | - | 2026 | 11.519 | 284.4 | 3.4 | 3.4 | 30% | 3 | 196 | - | - | - | - | - |  |  | -33.8841 | 18.5336
base | Ankerlig | gas | Generator | Existing | 1332 | 148 | 9 | - | 2039 | 11.519 | 263.4 | 9 | 9 | 30% | 3 | 196 | - | - | - | - | - |  |  | -33.592 | 18.4607
base | Gourikwa | gas | Generator | Existing | 740 | 148 | 5 | - | 2038 | 11.519 | 263.4 | 9 | 9 | 30% | 3 | 196 | - | - | - | - | - |  |  | -34.1653 | 21.9608
base | PortRex | gas | Generator | Existing | 171 | 57 | 3 | - | 2026 | 11.519 | 284.4 | 3.4 | 3.4 | 30% | 3 | 196 | - | - | - | - | - |  |  | -33.0274 | 27.8838
2Gt | Arnot* | coal | Generator | Existing | 1116 | 372 | 3 | - | 2027 | 12.744 | 25.9 | 2.1 | 2.1 | 0% | 98 | 1133 | - | - | - | - | - |  |  | -25.9444 | 29.7917
2Gt | Arnot** | coal | Generator | Existing | 1116 | 372 | 3 | - | 2030 | 12.744 | 25.9 | 2.1 | 2.1 | 0% | 98 | 1133 | - | - | - | - | - | 0 | 0 | -25.9444 | 29.7917
2Gt | Camden* | coal | Generator | Existing | 740 | 370 | 2 | - | 2022 | 13.584 | 32.3 | 1.1 | 1.1 | 0% | 98 | 1133 | - | - | - | - | - |  |  | -26.6201 | 30.0911
2Gt | Camden** | coal | Generator | Existing | 370 | 370 | 1 | - | 2024 | 14.28 | 32.3 | 1.1 | 1.1 | 0% | 98 | 1133 | - | - | - | - | - |  |  | -26.6201 | 30.0911
2Gt | Duvha* | coal | Generator | Existing | 1725 | 575 | 3 | - | 2032 | 12.066 | 18 | 3.3 | 3.3 | 0% | 98 | 1133 | - | - | - | - | - |  |  | -25.9595 | 29.3409
2Gt | Duvha** | coal | Generator | Existing | 1150 | 575 | 2 |  | 2035 | 12.066 | 18 | 3.3 | 3.3 | 0% | 98 | 1133 | - | - | - | - | - | 0 | 0 | -25.9595 | 29.3409
2Gt | Grootvlei* | coal | Generator | Existing | 286 | 143 | 2 | - | 2019 | 13.79 | 29.8 | 0.9 | 0.9 | 0% | 98 | 1133 | - | - | - | - | - |  |  | -26.7695 | 28.4995
2Gt | Grootvlei** | coal | Generator | Existing | 286 | 143 | 2 |  | 2020 | 13.79 | 29.8 | 0.9 | 0.9 | 0% | 98 | 1133 | - | - | - | - | - | 0 | 0 | -26.7695 | 28.4995
2Gt | Hendrina* | coal | Generator | Existing | 440 | 110 | 4 | - | 2021 | 13.266 | 28.7 | 1.1 | 1.1 | 0% | 98 | 1133 | - | - | - | - | - |  |  | -26.0314 | 29.6014
2Gt | Hendrina** | coal | Generator | Existing | 440 | 110 | 4 |  | 2023 | 13.266 | 28.7 | 1.1 | 1.1 | 0% | 98 | 1133 | - | - | - | - | - | 0 | 0 | -26.0314 | 29.6014
2Gt | Kendal* | coal | Generator | Existing | 1920 | 640 | 3 | - | 2041 | 11.782 | 24.3 | 1.8 | 1.8 | 0% | 98 | 1133 | - | - | - | - | - |  |  | -26.088 | 28.9689
2Gt | Kendal** | coal | Generator | Existing | 1920 | 640 | 3 |  | 2044 | 11.782 | 24.3 | 1.8 | 1.8 | 0% | 98 | 1133 | - | - | - | - | - | 0 | 0 | -26.088 | 28.9689
2Gt | Komati | coal | Generator | Existing | 114 | 114 | 1 | - | 2022 | 15.123 | 34.7 | 0.5 | 0.5 | 0% | 98 | 1133 | - | - | - | - | - |  |  | -26.0908 | 29.4745
2Gt | Kriel* | coal | Generator | Existing | 1425 | 475 | 3 | - | 2024 | 12.995 | 28.6 | 3.6 | 3.6 | 0% | 98 | 1133 | - | - | - | - | - |  |  | -26.254 | 29.1801
2Gt | Kriel** | coal | Generator | Existing | 1425 | 475 | 3 |  | 2028 | 12.995 | 28.6 | 3.6 | 3.6 | 0% | 98 | 1133 | - | - | - | - | - | 0 | 0 | -26.254 | 29.1801
2Gt | Kusile* | coal | Generator | Existing | 2400 | 600 | 4 | - | beyond 2050 | 10.305 | 31.6 | 7.2 | 7.2 | 30% | 98 | 1133 | - | - | - | - | - |  |  | -25.5459 | 28.5502
2Gt | Kusile** | coal | Generator | Existing | 600 | 600 | 1 | 2023 | beyond 2050 | 10.305 | 31.6 | 7.2 | 7.2 | 30% | 98 | 1133 | - | - | - | - | - | 0 | 0 | -25.5459 | 28.5502
2Gt | Kusile*** | coal | Generator | Existing | 600 | 600 | 1 | 2024 | beyond 2050 | 10.305 | 31.6 | 7.2 | 7.2 | 30% | 98 | 1133 | - | - | - | - | - | 0 | 0 | -25.5459 | 28.5502
2Gt | Lethabo* | coal | Generator | Existing | 1779 | 593 | 3 | - | 2039 | 11.003 | 14.4 | 5.9 | 5.9 | 0% | 98 | 1133 | - | - | - | - | - |  |  | -26.7403 | 27.975
2Gt | Lethabo** | coal | Generator | Existing | 1779 | 593 | 3 |  | 2042 | 11.003 | 14.4 | 5.9 | 5.9 | 0% | 98 | 1133 | - | - | - | - | - | 0 | 0 | -26.7403 | 27.975
2Gt | Majuba* | coal | Generator | Existing | 1833 | 611 | 3 | - | 2031 | 11.782 | 32.1 | 1.7 | 1.7 | 0% | 98 | 1133 | - | - | - | - | - |  |  | -27.0955 | 29.7706
2Gt | Majuba** | coal | Generator | Existing | 2010 | 670 | 3 | - | 2050 | 11.032 | 32.1 | 1.9 | 1.9 | 0% | 98 | 1133 | - | - | - | - | - |  |  | -27.0955 | 29.7706
2Gt | Matimba* | coal | Generator | Existing | 1845 | 615 | 3 | - | 2040 | 11.682 | 17.5 | 3 | 3 | 0% | 98 | 1133 | - | - | - | - | - |  |  | -23.6678 | 27.6128
2Gt | Matimba** | coal | Generator | Existing | 1845 | 615 | 3 |  | 2043 | 11.682 | 17.5 | 3 | 3 | 0% | 98 | 1133 | - | - | - | - | - | 0 | 0 | -23.6678 | 27.6128
2Gt | Matla* | coal | Generator | Existing | 1725 | 575 | 3 | - | 2032 | 12.066 | 30.2 | 2.4 | 2.4 | 0% | 98 | 1133 | - | - | - | - | - |  |  | -26.2804 | 29.1423
2Gt | Matla** | coal | Generator | Existing | 1725 | 575 | 3 |  | 2034 | 12.066 | 30.2 | 2.4 | 2.4 | 0% | 98 | 1133 | - | - | - | - | - | 0 | 0 | -26.2804 | 29.1423
2Gt | Medupi* | coal | Generator | Existing | 3000 | 600 | 5 | - | beyond 2050 | 10.305 | 21.4 | 7.2 | 7.2 | 30% | 98 | 1133 | - | - | - | - | - |  |  | -23.42 | 27.33
2Gt | Medupi** | coal | Generator | Existing | 600 | 600 | 1 |  | beyond 2050 | 10.305 | 21.4 | 7.2 | 7.2 | 30% | 98 | 1133 | - | - | - | - | - | 0 | 0 | -23.42 | 27.33
2Gt | Tutuka* | coal | Generator | Existing | 1755 | 585 | 3 | - | 2040 | 10.495 | 32.3 | 3.2 | 3.2 | 0% | 98 | 1133 | - | - | - | - | - |  |  | -26.7756 | 29.3521
2Gt | Tutuka** | coal | Generator | Existing | 1755 | 585 | 3 |  | 2042 | 10.495 | 32.3 | 3.2 | 3.2 | 0% | 98 | 1133 | - | - | - | - | - | 0 | 0 | -26.7756 | 29.3521
2Gt | Sere | onwind | Generator | Existing | 100 | 2 | 50 | - | 2034 | - | - | - | - | 0% | 737 | 0 | - | - | - | - | - |  |  | -31.5018 | 18.1143
2Gt | Koeberg | nuclear | Generator | Existing | 1854 | 930 | 2 | - | 2047 | 11.111 | 8.5 | - | - | 50% | 45 | 1187 | - | - | - | - | - |  |  | -33.6737 | 18.4281
2Gt | Drakensberg | PHS | StorageUnit | Existing | 1000 | 250 | 4 | - | beyond 2050 | - | - | - | - | 0% | 0.0001 | 222 | 0.737 | 4 | 250 | 21.7 | - |  |  | -28.5628 | 29.0828
2Gt | Ingula | PHS | StorageUnit | Existing | 1332 | 333 | 4 | - | beyond 2050 | - | - | - | - | 0% | 0.0002 | 2796 | 78% | 4 | 333 | 27.4 | - |  |  | -28.165 | 29.3512
2Gt | Palmiet | PHS | StorageUnit | Existing | 400 | 200 | 2 | - | beyond 2050 | - | - | - | - | 0% | 0.0003 | 222 | 0.779 | 2 | 200 | 10 | - |  |  | -34.1972 | 18.9736
2Gt | Gariep | hydro | Generator | Existing | 360 | 90 | 4 | - | beyond 2050 | - | - | - | - | 0% | 350 | 0 | - | - | - | - | - |  |  | -30.624 | 25.504
2Gt | Vanderkloof | hydro | Generator | Existing | 240 | 120 | 2 | - | beyond 2050 | - | - | - | - | 0% | 350 | 0 | - | - | - | - | - |  |  | -29.9934 | 24.7338
2Gt | Acacia | gas | Generator | Existing | 171 | 57 | 3 | - | 2026 | 11.519 | 284.4 | 3.4 | 3.4 | 0% | 3 | 196 | - | - | - | - | - |  |  | -33.8841 | 18.5336
2Gt | Ankerlig | gas | Generator | Existing | 1332 | 148 | 9 | - | 2039 | 11.519 | 263.4 | 9 | 9 | 0% | 3 | 196 | - | - | - | - | - |  |  | -33.592 | 18.4607
2Gt | Gourikwa | gas | Generator | Existing | 740 | 148 | 5 | - | 2038 | 11.519 | 263.4 | 9 | 9 | 0% | 3 | 196 | - | - | - | - | - |  |  | -34.1653 | 21.9608
2Gt | PortRex | gas | Generator | Existing | 171 | 57 | 3 | - | 2026 | 11.519 | 284.4 | 3.4 | 3.4 | 0% | 3 | 196 | - | - | - | - | - |  |  | -33.0274 | 27.8838
LC-Retirement | Arnot* | coal | Generator | Existing | 1116 | 372 | 3 | - | 2026 | 12.744 | 25.9 | 2.1 | 2.1 | 30% | 98 | 1133 | - | - | - | - | - |  |  | -25.9444 | 29.7917
LC-Retirement | Arnot** | coal | Generator | Existing | 1116 | 372 | 3 | - | 2030 | 12.744 | 25.9 | 2.1 | 2.1 | 30% | 98 | 1133 | - | - | - | - | - | 0 | 0 | -25.9444 | 29.7917
LC-Retirement | Camden* | coal | Generator | Existing | 740 | 370 | 2 | - | 2021 | 13.584 | 32.3 | 1.1 | 1.1 | 30% | 98 | 1133 | - | - | - | - | - |  |  | -26.6201 | 30.0911
LC-Retirement | Camden** | coal | Generator | Existing | 370 | 370 | 1 | - | 2024 | 14.28 | 32.3 | 1.1 | 1.1 | 30% | 98 | 1133 | - | - | - | - | - |  |  | -26.6201 | 30.0911
LC-Retirement | Duvha* | coal | Generator | Existing | 1150 | 575 | 2 | - | 2031 | 12.066 | 18 | 3.3 | 3.3 | 30% | 98 | 1133 | - | - | - | - | - |  |  | -25.9595 | 29.3409
LC-Retirement | Duvha** | coal | Generator | Existing | 1725 | 575 | 3 | - | 2034 | 12.066 | 18 | 3.3 | 3.3 | 30% | 98 | 1133 | - | - | - | - | - | 0 | 0 | -25.9595 | 29.3409
LC-Retirement | Grootvlei* | coal | Generator | Existing | 286 | 143 | 2 | - | 2019 | 13.79 | 29.8 | 0.9 | 0.9 | 30% | 98 | 1133 | - | - | - | - | - |  |  | -26.7695 | 28.4995
LC-Retirement | Grootvlei** | coal | Generator | Existing | 286 | 143 | 2 | - | 2020 | 13.79 | 29.8 | 0.9 | 0.9 | 30% | 98 | 1133 | - | - | - | - | - | 0 | 0 | -26.7695 | 28.4995
LC-Retirement | Hendrina* | coal | Generator | Existing | 440 | 110 | 4 | - | 2021 | 13.266 | 28.7 | 1.1 | 1.1 | 30% | 98 | 1133 | - | - | - | - | - |  |  | -26.0314 | 29.6014
LC-Retirement | Hendrina** | coal | Generator | Existing | 440 | 110 | 4 | - | 2022 | 13.266 | 28.7 | 1.1 | 1.1 | 30% | 98 | 1133 | - | - | - | - | - | 0 | 0 | -26.0314 | 29.6014
LC-Retirement | Kendal* | coal | Generator | Existing | 1920 | 640 | 3 | - | 2041 | 11.782 | 24.3 | 1.8 | 1.8 | 30% | 98 | 1133 | - | - | - | - | - |  |  | -26.088 | 28.9689
LC-Retirement | Kendal** | coal | Generator | Existing | 1920 | 640 | 3 | - | 2044 | 11.782 | 24.3 | 1.8 | 1.8 | 30% | 98 | 1133 | - | - | - | - | - | 0 | 0 | -26.088 | 28.9689
LC-Retirement | Komati | coal | Generator | Existing | 114 | 114 | 1 | - | 2022 | 15.123 | 34.7 | 0.5 | 0.5 | 30% | 98 | 1133 | - | - | - | - | - |  |  | -26.0908 | 29.4745
LC-Retirement | Kriel* | coal | Generator | Existing | 1425 | 475 | 3 | - | 2027 | 12.995 | 28.6 | 3.6 | 3.6 | 30% | 98 | 1133 | - | - | - | - | - |  |  | -26.254 | 29.1801
LC-Retirement | Kriel** | coal | Generator | Existing | 1425 | 475 | 3 |  | 2030 | 12.995 | 28.6 | 3.6 | 3.6 | 30% | 98 | 1133 | - | - | - | - | - | 0 | 0 | -26.254 | 29.1801
LC-Retirement | Kusile* | coal | Generator | Existing | 2880 | 720 | 4 | - | beyond 2050 | 10.305 | 31.6 | 7.2 | 7.2 | 30% | 98 | 1133 | - | - | - | - | - |  |  | -25.5459 | 28.5502
LC-Retirement | Kusile** | coal | Generator | Existing | 720 | 720 | 1 | 2023 | beyond 2050 | 10.305 | 31.6 | 7.2 | 7.2 | 30% | 98 | 1133 | - | - | - | - | - | 0 | 0 | -25.5459 | 28.5502
LC-Retirement | Kusile*** | coal | Generator | Existing | 720 | 720 | 1 | 2024 | beyond 2050 | 10.305 | 31.6 | 7.2 | 7.2 | 30% | 98 | 1133 | - | - | - | - | - | 0 | 0 | -25.5459 | 28.5502
LC-Retirement | Lethabo* | coal | Generator | Existing | 2372 | 593 | 4 | - | 2037 | 11.003 | 14.4 | 5.9 | 5.9 | 30% | 98 | 1133 | - | - | - | - | - |  |  | -26.7403 | 27.975
LC-Retirement | Lethabo** | coal | Generator | Existing | 1186 | 593 | 2 | - | 2041 | 11.003 | 14.4 | 5.9 | 5.9 | 30% | 98 | 1133 | - | - | - | - | - | 0 | 0 | -26.7403 | 27.975
LC-Retirement | Majuba* | coal | Generator | Existing | 1833 | 611 | 3 | - | 2047 | 11.782 | 32.1 | 1.7 | 1.7 | 30% | 98 | 1133 | - | - | - | - | - |  |  | -27.0955 | 29.7706
LC-Retirement | Majuba** | coal | Generator | Existing | 2010 | 670 | 3 | - | 2051 | 11.032 | 32.1 | 1.9 | 1.9 | 30% | 98 | 1133 | - | - | - | - | - |  |  | -27.0955 | 29.7706
LC-Retirement | Matimba* | coal | Generator | Existing | 1230 | 615 | 2 | - | 2038 | 11.682 | 17.5 | 3 | 3 | 30% | 98 | 1133 | - | - | - | - | - |  |  | -23.6678 | 27.6128
LC-Retirement | Matimba** | coal | Generator | Existing | 2460 | 615 | 4 | - | 2042 | 11.682 | 17.5 | 3 | 3 | 30% | 98 | 1133 | - | - | - | - | - | 0 | 0 | -23.6678 | 27.6128
LC-Retirement | Matla* | coal | Generator | Existing | 1725 | 575 | 3 | - | 2031 | 12.066 | 30.2 | 2.4 | 2.4 | 30% | 98 | 1133 | - | - | - | - | - |  |  | -26.2804 | 29.1423
LC-Retirement | Matla** | coal | Generator | Existing | 1725 | 575 | 3 | - | 2033 | 12.066 | 30.2 | 2.4 | 2.4 | 30% | 98 | 1133 | - | - | - | - | - | 0 | 0 | -26.2804 | 29.1423
LC-Retirement | Medupi* | coal | Generator | Existing | 3615 | 723 | 5 | - | beyond 2050 | 10.305 | 21.4 | 7.2 | 7.2 | 30% | 98 | 1133 | - | - | - | - | - |  |  | -23.42 | 27.33
LC-Retirement | Medupi** | coal | Generator | Existing | 723 | 723 | 1 | - | beyond 2050 | 10.305 | 21.4 | 7.2 | 7.2 | 30% | 98 | 1133 | - | - | - | - | - | 0 | 0 | -23.42 | 27.33
LC-Retirement | Tutuka* | coal | Generator | Existing | 1170 | 585 | 2 | - | 2032 | 10.495 | 32.3 | 3.2 | 3.2 | 30% | 98 | 1133 | - | - | - | - | - |  |  | -26.7756 | 29.3521
LC-Retirement | Tutuka** | coal | Generator | Existing | 2340 | 585 | 4 | - | 2040 | 10.495 | 32.3 | 3.2 | 3.2 | 30% | 98 | 1133 | - | - | - | - | - | 0 | 0 | -26.7756 | 29.3521
LC-Retirement | Sere | onwind | Generator | Existing | 100 | 2 | 50 | - | 2035 | - | - | - | - | 30% | 737 | 0 | - | - | - | - | - |  |  | -31.5018 | 18.1143
LC-Retirement | Koeberg | nuclear | Generator | Existing | 1854 | 930 | 2 | - | 2047 | 11.111 | 8.5 | - | - | 30% | 45 | 1187 | - | - | - | - | - |  |  | -33.6737 | 18.4281
LC-Retirement | Drakensberg | PHS | StorageUnit | Existing | 1000 | 250 | 4 | - | beyond 2050 | - | - | - | - | 30% | 0.0001 | 222 | 73.7% | 4 | 250 | 21.7 | - |  |  | -28.5628 | 29.0828
LC-Retirement | Ingula | PHS | StorageUnit | Existing | 1332 | 333 | 4 | - | beyond 2050 | - | - | - | - | 30% | 0.0002 | 2796 | 78% | 4 | 333 | 27.4 | - |  |  | -28.165 | 29.3512
LC-Retirement | Palmiet | PHS | StorageUnit | Existing | 400 | 200 | 2 | - | beyond 2050 | - | - | - | - | 30% | 0.0003 | 222 | 77.9% | 2 | 200 | 10 | - |  |  | -34.1972 | 18.9736
LC-Retirement | Gariep | hydro | Generator | Existing | 360 | 90 | 4 | - | beyond 2050 | - | - | - | - | 30% | 350 | 0 | - | - | - | - | - |  |  | -30.624 | 25.504
LC-Retirement | Vanderkloof | hydro | Generator | Existing | 240 | 120 | 2 | - | beyond 2050 | - | - | - | - | 30% | 350 | 0 | - | - | - | - | - |  |  | -29.9934 | 24.7338
LC-Retirement | Acacia | gas | Generator | Existing | 171 | 57 | 3 | - | 2026 | 11.519 | 284.4 | 3.4 | 3.4 | 30% | 3 | 196 | - | - | - | - | - |  |  | -33.8841 | 18.5336
LC-Retirement | Ankerlig | gas | Generator | Existing | 1332 | 148 | 9 | - | 2039 | 11.519 | 263.4 | 9 | 9 | 30% | 3 | 196 | - | - | - | - | - |  |  | -33.592 | 18.4607
LC-Retirement | Gourikwa | gas | Generator | Existing | 740 | 148 | 5 | - | 2038 | 11.519 | 263.4 | 9 | 9 | 30% | 3 | 196 | - | - | - | - | - |  |  | -34.1653 | 21.9608
LC-Retirement | PortRex | gas | Generator | Existing | 171 | 57 | 3 | - | 2026 | 11.519 | 284.4 | 3.4 | 3.4 | 30% | 3 | 196 | - | - | - | - | - |  |  | -33.0274 | 27.8838
2Gt-Retirement | Arnot* | coal | Generator | Existing | 1116 | 372 | 3 | - | 2023 | 12.744 | 25.9 | 2.1 | 2.1 | 0% | 98 | 1133 | - | - | - | - | - |  |  | -25.9444 | 29.7917
2Gt-Retirement | Arnot** | coal | Generator | Existing | 1116 | 372 | 3 | - | 2030 | 12.744 | 25.9 | 2.1 | 2.1 | 0% | 98 | 1133 | - | - | - | - | - | 0 | 0 | -25.9444 | 29.7917
2Gt-Retirement | Camden* | coal | Generator | Existing | 740 | 370 | 2 | - | 2021 | 13.584 | 32.3 | 1.1 | 1.1 | 0% | 98 | 1133 | - | - | - | - | - |  |  | -26.6201 | 30.0911
2Gt-Retirement | Camden** | coal | Generator | Existing | 370 | 370 | 1 | - | 2024 | 14.28 | 32.3 | 1.1 | 1.1 | 0% | 98 | 1133 | - | - | - | - | - |  |  | -26.6201 | 30.0911
2Gt-Retirement | Duvha* | coal | Generator | Existing | 1150 | 575 | 2 | - | 2031 | 12.066 | 18 | 3.3 | 3.3 | 0% | 98 | 1133 | - | - | - | - | - |  |  | -25.9595 | 29.3409
2Gt-Retirement | Duvha** | coal | Generator | Existing | 1725 | 575 | 3 | - | 2034 | 12.066 | 18 | 3.3 | 3.3 | 0% | 98 | 1133 | - | - | - | - | - | 0 | 0 | -25.9595 | 29.3409
2Gt-Retirement | Grootvlei* | coal | Generator | Existing | 286 | 143 | 2 | - | 2019 | 13.79 | 29.8 | 0.9 | 0.9 | 0% | 98 | 1133 | - | - | - | - | - |  |  | -26.7695 | 28.4995
2Gt-Retirement | Grootvlei** | coal | Generator | Existing | 286 | 143 | 2 | - | 2020 | 13.79 | 29.8 | 0.9 | 0.9 | 0% | 98 | 1133 | - | - | - | - | - | 0 | 0 | -26.7695 | 28.4995
2Gt-Retirement | Hendrina* | coal | Generator | Existing | 440 | 110 | 4 | - | 2021 | 13.266 | 28.7 | 1.1 | 1.1 | 0% | 98 | 1133 | - | - | - | - | - |  |  | -26.0314 | 29.6014
2Gt-Retirement | Hendrina** | coal | Generator | Existing | 440 | 110 | 4 | - | 2022 | 13.266 | 28.7 | 1.1 | 1.1 | 0% | 98 | 1133 | - | - | - | - | - | 0 | 0 | -26.0314 | 29.6014
2Gt-Retirement | Kendal* | coal | Generator | Existing | 1920 | 640 | 3 | - | 2023 | 11.782 | 24.3 | 1.8 | 1.8 | 0% | 98 | 1133 | - | - | - | - | - |  |  | -26.088 | 28.9689
2Gt-Retirement | Kendal** | coal | Generator | Existing | 1920 | 640 | 3 | - | 2037 | 11.782 | 24.3 | 1.8 | 1.8 | 0% | 98 | 1133 | - | - | - | - | - | 0 | 0 | -26.088 | 28.9689
2Gt-Retirement | Komati | coal | Generator | Existing | 114 | 114 | 1 | - | 2022 | 15.123 | 34.7 | 0.5 | 0.5 | 0% | 98 | 1133 | - | - | - | - | - |  |  | -26.0908 | 29.4745
2Gt-Retirement | Kriel* | coal | Generator | Existing | 1425 | 475 | 3 | - | 2027 | 12.995 | 28.6 | 3.6 | 3.6 | 0% | 98 | 1133 | - | - | - | - | - |  |  | -26.254 | 29.1801
2Gt-Retirement | Kriel** | coal | Generator | Existing | 1425 | 475 | 3 |  | 2030 | 12.995 | 28.6 | 3.6 | 3.6 | 0% | 98 | 1133 | - | - | - | - | - | 0 | 0 | -26.254 | 29.1801
2Gt-Retirement | Kusile* | coal | Generator | Existing | 2880 | 720 | 4 | - | 2040 | 10.305 | 31.6 | 7.2 | 7.2 | 0% | 98 | 1133 | - | - | - | - | - |  |  | -25.5459 | 28.5502
2Gt-Retirement | Kusile** | coal | Generator | Existing | 720 | 720 | 1 | 2023 | 2040 | 10.305 | 31.6 | 7.2 | 7.2 | 0% | 98 | 1133 | - | - | - | - | - | 0 | 0 | -25.5459 | 28.5502
2Gt-Retirement | Kusile*** | coal | Generator | Existing | 720 | 720 | 1 | 2024 | 2040 | 10.305 | 31.6 | 7.2 | 7.2 | 0% | 98 | 1133 | - | - | - | - | - | 0 | 0 | -25.5459 | 28.5502
2Gt-Retirement | Lethabo* | coal | Generator | Existing | 2372 | 593 | 4 | - | 2037 | 11.003 | 14.4 | 5.9 | 5.9 | 0% | 98 | 1133 | - | - | - | - | - |  |  | -26.7403 | 27.975
2Gt-Retirement | Lethabo** | coal | Generator | Existing | 1186 | 593 | 2 | - | 2041 | 11.003 | 14.4 | 5.9 | 5.9 | 0% | 98 | 1133 | - | - | - | - | - | 0 | 0 | -26.7403 | 27.975
2Gt-Retirement | Majuba* | coal | Generator | Existing | 1833 | 611 | 3 | - | 2022 | 11.782 | 32.1 | 1.7 | 1.7 | 0% | 98 | 1133 | - | - | - | - | - |  |  | -27.0955 | 29.7706
2Gt-Retirement | Majuba** | coal | Generator | Existing | 2010 | 670 | 3 | - | 2030 | 11.032 | 32.1 | 1.9 | 1.9 | 0% | 98 | 1133 | - | - | - | - | - |  |  | -27.0955 | 29.7706
2Gt-Retirement | Matimba* | coal | Generator | Existing | 1230 | 615 | 2 | - | 2026 | 11.682 | 17.5 | 3 | 3 | 0% | 98 | 1133 | - | - | - | - | - |  |  | -23.6678 | 27.6128
2Gt-Retirement | Matimba** | coal | Generator | Existing | 2460 | 615 | 4 | - | 2040 | 11.682 | 17.5 | 3 | 3 | 0% | 98 | 1133 | - | - | - | - | - | 0 | 0 | -23.6678 | 27.6128
2Gt-Retirement | Matla* | coal | Generator | Existing | 1725 | 575 | 3 | - | 2022 | 12.066 | 30.2 | 2.4 | 2.4 | 0% | 98 | 1133 | - | - | - | - | - |  |  | -26.2804 | 29.1423
2Gt-Retirement | Matla** | coal | Generator | Existing | 1725 | 575 | 3 | - | 2025 | 12.066 | 30.2 | 2.4 | 2.4 | 0% | 98 | 1133 | - | - | - | - | - | 0 | 0 | -26.2804 | 29.1423
2Gt-Retirement | Medupi* | coal | Generator | Existing | 3615 | 723 | 5 | - | beyond 2050 | 10.305 | 21.4 | 7.2 | 7.2 | 0% | 98 | 1133 | - | - | - | - | - |  |  | -23.42 | 27.33
2Gt-Retirement | Medupi** | coal | Generator | Existing | 723 | 723 | 1 | - | beyond 2050 | 10.305 | 21.4 | 7.2 | 7.2 | 0% | 98 | 1133 | - | - | - | - | - | 0 | 0 | -23.42 | 27.33
2Gt-Retirement | Tutuka* | coal | Generator | Existing | 1170 | 585 | 2 | - | 2022 | 10.495 | 32.3 | 3.2 | 3.2 | 0% | 98 | 1133 | - | - | - | - | - |  |  | -26.7756 | 29.3521
2Gt-Retirement | Tutuka** | coal | Generator | Existing | 2340 | 585 | 4 | - | 2024 | 10.495 | 32.3 | 3.2 | 3.2 | 0% | 98 | 1133 | - | - | - | - | - | 0 | 0 | -26.7756 | 29.3521
2Gt-Retirement | Sere | onwind | Generator | Existing | 100 | 2 | 50 | - | 2035 | - | - | - | - | 0% | 737 | 0 | - | - | - | - | - |  |  | -31.5018 | 18.1143
2Gt-Retirement | Koeberg | nuclear | Generator | Existing | 1854 | 930 | 2 | - | 2047 | 11.111 | 8.5 | - | - | 0% | 45 | 1187 | - | - | - | - | - |  |  | -33.6737 | 18.4281
2Gt-Retirement | Drakensberg | PHS | StorageUnit | Existing | 1000 | 250 | 4 | - | beyond 2050 | - | - | - | - | 0% | 0.0001 | 222 | 73.7% | 4 | 250 | 21.7 | - |  |  | -28.5628 | 29.0828
2Gt-Retirement | Ingula | PHS | StorageUnit | Existing | 1332 | 333 | 4 | - | beyond 2050 | - | - | - | - | 0% | 0.0002 | 2796 | 78% | 4 | 333 | 27.4 | - |  |  | -28.165 | 29.3512
2Gt-Retirement | Palmiet | PHS | StorageUnit | Existing | 400 | 200 | 2 | - | beyond 2050 | - | - | - | - | 0% | 0.0003 | 222 | 77.9% | 2 | 200 | 10 | - |  |  | -34.1972 | 18.9736
2Gt-Retirement | Gariep | hydro | Generator | Existing | 360 | 90 | 4 | - | beyond 2050 | - | - | - | - | 0% | 350 | 0 | - | - | - | - | - |  |  | -30.624 | 25.504
2Gt-Retirement | Vanderkloof | hydro | Generator | Existing | 240 | 120 | 2 | - | beyond 2050 | - | - | - | - | 0% | 350 | 0 | - | - | - | - | - |  |  | -29.9934 | 24.7338
2Gt-Retirement | Acacia | gas | Generator | Existing | 171 | 57 | 3 | - | 2026 | 11.519 | 284.4 | 3.4 | 3.4 | 0% | 3 | 196 | - | - | - | - | - |  |  | -33.8841 | 18.5336
2Gt-Retirement | Ankerlig | gas | Generator | Existing | 1332 | 148 | 9 | - | 2039 | 11.519 | 263.4 | 9 | 9 | 0% | 3 | 196 | - | - | - | - | - |  |  | -33.592 | 18.4607
2Gt-Retirement | Gourikwa | gas | Generator | Existing | 740 | 148 | 5 | - | 2038 | 11.519 | 263.4 | 9 | 9 | 0% | 3 | 196 | - | - | - | - | - |  |  | -34.1653 | 21.9608
2Gt-Retirement | PortRex | gas | Generator | Existing | 171 | 57 | 3 | - | 2026 | 11.519 | 284.4 | 3.4 | 3.4 | 0% | 3 | 196 | - | - | - | - | - |  |  | -33.0274 | 27.8838

## existing_non_eskom
| Power Station Name | Grouping | Carrier | Type | Status | Capacity (MW) | Unit size (MW) | Number units | Future Commissioning Date | Decommissioning Date | Heat Rate (GJ/MWh) | Fuel Price (R/GJ) | Max Ramp Up (MW/min) | Max Ramp Down (MW/min) | Min Stable Level (%) | Variable O&M Cost (R/MWh) | Fixed O&M Cost (R/kW/yr) | Pump Efficiency (%) | Pump Units | Pump Load per unit (MW) | Pumped Storage - Max Storage (GWh) | CSP Storage (hours) | GPS Latitude | GPS Longitude
base | Aries Solar Energy Facility | aga | solar | Generator | Existing | 9.65 | - | - | - | 2039 | - | - | - | - | 0% | 3649 | 0 | - | - | - | - | - | -29.3501 | 21.154
base | Cookhouse Wind Farm | aga | onwind | Generator | Existing | 135.8 | - | - | - | 2034 | - | - | - | - | 0% | 1513 | 0 | - | - | - | - | - | -32.7461 | 25.807
base | Dassieklip Wind Energy Facility | aga | onwind | Generator | Existing | 27 | - | - | - | 2034 | - | - | - | - | 0% | 1513 | 0 | - | - | - | - | - | -34.2324 | 19.4288
base | De Aar Solar Power | aga | solar | Generator | Existing | 45.6 | - | - | - | 2039 | - | - | - | - | 0% | 3649 | 0 | - | - | - | - | - | -30.6599 | 24.0198
base | Dorper Wind Farm | aga | onwind | Generator | Existing | 97.53 | - | - | - | 2034 | - | - | - | - | 0% | 1513 | 0 | - | - | - | - | - | -31.3963 | 26.3538
base | Greefspan PV Power Plant | aga | solar | Generator | Existing | 9.9 | - | - | - | 2039 | - | - | - | - | 0% | 3649 | 0 | - | - | - | - | - | -29.1151 | 23.7491
base | Herbert PV Power Plant | aga | solar | Generator | Existing | 19.9 | - | - | - | 2039 | - | - | - | - | 0% | 3649 | 0 | - | - | - | - | - | -29.1151 | 23.7491
base | Jeffreys Bay Wind Farm | aga | onwind | Generator | Existing | 135.11 | - | - | - | 2034 | - | - | - | - | 0% | 1513 | 0 | - | - | - | - | - | -34.0505 | 24.9061
base | Kalkbult | aga | solar | Generator | Existing | 72.4 | - | - | - | 2039 | - | - | - | - | 0% | 3649 | 0 | - | - | - | - | - | -30.4379 | 24.4704
base | Kaxu Solar One | aga | CSP | Generator | Existing | 100 | - | - | - | 2045 | - | - | - | - | 0% | 3554 | 0 | - | - | - | - | 3 | -28.5252 | 19.3535
base | Khi Solar One | aga | CSP | Generator | Existing | 50 |  |  | - | 2045 | - | - | - | - | 0% | 3554 | 0 | - | - | - | - | 6 | -28.3214 | 21.439
base | Konkoonsies Solar Energy Facility | aga | solar | Generator | Existing | 9.65 | - | - | - | 2039 | - | - | - | - | 0% | 3649 | 0 | - | - | - | - | - | -29.1621 | 19.3863
base | Kouga Wind Farm | aga | onwind | Generator | Existing | 77.7 | - | - | - | 2034 | - | - | - | - | 0% | 1513 | 0 | - | - | - | - | - | -34.0016 | 24.7416
base | Lesedi Power Company | aga | solar | Generator | Existing | 64 | - | - | - | 2039 | - | - | - | - | 0% | 3649 | 0 | - | - | - | - | - | -28.3095 | 23.1041
base | Letsatsi Power Company | aga | solar | Generator | Existing | 64 | - | - | - | 2039 | - | - | - | - | 0% | 3649 | 0 | - | - | - | - | - | -29.1121 | 26.2157
base | Metrowind Van Stadens Wind Farm | aga | onwind | Generator | Existing | 27 | - | - | - | 2034 | - | - | - | - | 0% | 1513 | 0 | - | - | - | - | - | -33.8048 | 25.4905
base | Mulilo Renewable Energy Solar PV De Aar | aga | solar | Generator | Existing | 10 | - | - | - | 2039 | - | - | - | - | 0% | 3649 | 0 | - | - | - | - | - | -30.6599 | 24.0198
base | Mulilo Renewable Energy Solar PV Prieska | aga | solar | Generator | Existing | 19.12 | - | - | - | 2039 | - | - | - | - | 0% | 3649 | 0 | - | - | - | - | - | -29.9647 | 22.3394
base | Nobelsfontein Phase 1 | aga | onwind | Generator | Existing | 73.8 | - | - | - | 2034 | - | - | - | - | 0% | 1513 | 0 | - | - | - | - | - | -31.4222 | 23.1149
base | REISA | aga | solar | Generator | Existing | 75 | - | - | - | 2039 | - | - | - | - | 0% | 3649 | 0 | - | - | - | - | - | -27.7581 | 23.0159
base | RustMo1 Solar Farm | aga | solar | Generator | Existing | 6.93 | - | - | - | 2039 | - | - | - | - | 0% | 3649 | 0 | - | - | - | - | - | -25.6533 | 27.2498
base | Droogfontein Solar Power | aga | solar | Generator | Existing | 45.4 | - | - | - | 2039 | - | - | - | - | 0% | 3649 | 0 | - | - | - | - | - | -28.7251 | 24.7517
base | Slimsun Swartland Solar Park | aga | solar | Generator | Existing | 5 | - | - | - | 2039 | - | - | - | - | 0% | 3649 | 0 | - | - | - | - | - | -33.4578 | 18.7233
base | Solar Capital De Aar | aga | solar | Generator | Existing | 75 | - | - | - | 2039 | - | - | - | - | 0% | 3649 | 0 | - | - | - | - | - | -30.6599 | 24.0198
base | Soutpan Solar Park | aga | solar | Generator | Existing | 27.94 | - | - | - | 2039 | - | - | - | - | 0% | 3649 | 0 | - | - | - | - | - | -23.3694 | 29.3218
base | Touwsrivier Project | aga | solar | Generator | Existing | 36 | - | - | - | 2039 | - | - | - | - | 0% | 3649 | 0 | - | - | - | - | - | -33.3394 | 20.0293
base | Umoya Energy Wind Farm | aga | onwind | Generator | Existing | 65.4 | - | - | - | 2034 | - | - | - | - | 0% | 1513 | 0 | - | - | - | - | - | -33.0286 | 18.3075
base | Witkop Solar Park | aga | solar | Generator | Existing | 29.68 | - | - | - | 2039 | - | - | - | - | 0% | 3649 | 0 | - | - | - | - | - | -23.9023 | 29.4508
base | Amakhala Emoyeni | aga | onwind | Generator | Existing | 131.05 | - | - | - | 2037 | - | - | - | - | 0% | 1186 | 0 | - | - | - | - | - | -32.6878 | 26.1064
base | Aurora Wind Power | aga | onwind | Generator | Existing | 90.82 | - | - | - | 2037 | - | - | - | - | 0% | 1186 | 0 | - | - | - | - | - | -32.9079 | 17.9958
base | Aurora_Rietvlei Solar Power | aga | solar | Generator | Existing | 8.9 | - | - | - | 2042 | - | - | - | - | 0% | 2176 | 0 | - | - | - | - | - | -32.7096 | 18.4854
base | Bokpoort CSP project | aga | CSP | Generator | Existing | 50 | - | - | - | 2048 | - | - | - | - | 0% | 3324 | 0 | - | - | - | - | 9 | -28.8779 | 21.92
base | Boshoff Solar Park | aga | solar | Generator | Existing | 57 | - | - | - | 2042 | - | - | - | - | 0% | 2176 | 0 | - | - | - | - | - | -28.5392 | 25.2131
base | Chaba Wind Farm | aga | onwind | Generator | Existing | 21 | - | - | - | 2036 | - | - | - | - | 0% | 1186 | 0 | - | - | - | - | - | -32.5879 | 27.8792
base | Dreunberg | aga | solar | Generator | Existing | 69.6 | - | - | - | 2042 | - | - | - | - | 0% | 2176 | 0 | - | - | - | - | - | -30.9974 | 26.3302
base | Gouda Wind Project | aga | onwind | Generator | Existing | 135.5 | - | - | - | 2037 | - | - | - | - | 0% | 1186 | 0 | - | - | - | - | - | -33.2944 | 19.044
base | Grassridge Wind Farm | aga | onwind | Generator | Existing | 59.8 | - | - | - | 2037 | - | - | - | - | 0% | 1186 | 0 | - | - | - | - | - | -33.7957 | 25.6722
base | Jasper Power Company | aga | solar | Generator | Existing | 75 | - | - | - | 2042 | - | - | - | - | 0% | 2176 | 0 | - | - | - | - | - | -28.3095 | 23.1041
base | Linde | aga | solar | Generator | Existing | 36.8 | - | - | - | 2042 | - | - | - | - | 0% | 2176 | 0 | - | - | - | - | - | -31.0452 | 24.4418
base | Neusberg Hydro Electrical Project | aga | hydro | Generator | Existing | 10 | - | - | - | beyond 2050 | - | - | - | - | 0% | 1363 | 0 | - | - | - | - | - | -28.7527 | 20.5335
base | Sishen Solar Facility | aga | solar | Generator | Existing | 74 | - | - | - | 2042 | - | - | - | - | 0% | 2176 | 0 | - | - | - | - | - | -27.7581 | 23.0159
base | Solar Capital De Aar 3 | aga | solar | Generator | Existing | 75 | - | - | - | 2042 | - | - | - | - | 0% | 2176 | 0 | - | - | - | - | - | -30.6599 | 24.0198
base | Stortemelk Hydro | aga | hydro | Generator | Existing | 4.22 | - | - | - | beyond 2050 | - | - | - | - | 0% | 1363 | 0 | - | - | - | - | - | -28.5142 | 28.4101
base | Tsitsikamma Community Wind Farm | aga | onwind | Generator | Existing | 93.68 | - | - | - | 2037 | - | - | - | - | 0% | 1186 | 0 | - | - | - | - | - | -34.0151 | 24.3446
base | Upington Airport | aga | solar | Generator | Existing | 8.9 | - | - | - | 2042 | - | - | - | - | 0% | 2176 | 0 | - | - | - | - | - | -28.4149 | 21.2219
base | Vredendal Solar Park | aga | solar | Generator | Existing | 8.8 | - | - | - | 2042 | - | - | - | - | 0% | 2176 | 0 | - | - | - | - | - | -31.6556 | 18.5161
base | Waainek Wind Farm | aga | onwind | Generator | Existing | 23.28 | - | - | - | 2037 | - | - | - | - | 0% | 1186 | 0 | - | - | - | - | - | -33.309 | 26.5317
base | !XiNa Solar One | aga | CSP | Generator | Existing | 100 | - | - | - | 2049 | - | - | - | - | 0% | 3114 | 0 | - | - | - | - | 6 | -29.1621 | 19.3863
base | Adams Solar PV 2 | aga | solar | Generator | Existing | 75 | - | - | - | 2043 | - | - | - | - | 0% | 2176 | 0 | - | - | - | - | - | -27.2025 | 22.8468
base | ENERGY Joburg Landfill Gas to Electircity Project | aga | biomass | Generator | Existing | 7.56 | - | - | - | 2049 | - | 0 | - | - | 0% | 1109 | 0 | - | - | - | - | - | -26.195 | 28.0325
base | Karoshoek Solar One | aga | CSP | Generator | Existing | 100 | - | - | - | 2049 | - | - | - | - | 0% | 3114 | 0 | - | - | - | - | 6 | -28.4149 | 21.2219
base | Khobab Wind Farm | aga | onwind | Generator | Existing | 137.74 | - | - | - | 2038 | - | - | - | - | 0% | 868 | 0 | - | - | - | - | - | -30.9181 | 19.441
base | Loeriesfontein 2 Wind Farm | aga | onwind | Generator | Existing | 138.23 | - | - | - | 2038 | - | - | - | - | 0% | 868 | 0 | - | - | - | - | - | -30.9181 | 19.441
base | Longyuan Mulilo De Aar Maanhaarberg Wind Energy Facility | aga | onwind | Generator | Existing | 96.48 | - | - | - | 2038 | - | - | - | - | 0% | 868 | 0 | - | - | - | - | - | -30.6599 | 24.0198
base | Longyuan Mulilo Green Energy De Aar 2 North Wind Energy Facility | aga | onwind | Generator | Existing | 138.96 | - | - | - | 2038 | - | - | - | - | 0% | 868 | 0 | - | - | - | - | - | -30.6599 | 24.0198
base | Mkuze | aga | biomass | Generator | Planned | 16.5 | - | 32 | - | beyond 2050 | - | 1650 | - | - | 0% | 1500 | 0 | - | 6 | 4 |  |  | -27.618 | 32.0345
base | Mulilo Prieska PV | aga | solar | Generator | Existing | 75 | - | - | - | 2043 | - | - | - | - | 0% | 1165 | 0 | - | - | - | - | - | -29.9647 | 22.3394
base | Mulilo Sonnedix Prieska PV | aga | solar | Generator | Existing | 75 | - | - | - | 2043 | - | - | - | - | 0% | 1165 | 0 | - | - | - | - | - | -29.9647 | 22.3394
base | Nojoli Wind Farm | aga | onwind | Generator | Existing | 86.6 | - | - | - | 2038 | - | - | - | - | 0% | 868 | 0 | - | - | - | - | - | -32.7461 | 25.807
base | Noupoort Wind Farm | aga | onwind | Generator | Existing | 79.05 | - | - | - | 2038 | - | - | - | - | 0% | 868 | 0 | - | - | - | - | - | -31.1839 | 24.946
base | Paleisheuwel | aga | solar | Generator | Existing | 75 | - | - | - | 2043 | - | - | - | - | 0% | 1165 | 0 | - | - | - | - | - | -32.1967 | 18.895
base | Pulida Solar Park | aga | solar | Generator | Existing | 75 | - | - | - | 2043 | - | - | - | - | 0% | 1165 | 0 | - | - | - | - | - | -29.1333 | 24.7988
base | Red Cap Gibson Bay | aga | onwind | Generator | Existing | 108.25 | - | - | - | 2038 | - | - | - | - | 0% | 868 | 0 | - | - | - | - | - | -34.0016 | 24.7416
base | Tom Burke Solar Park | aga | solar | Generator | Existing | 60 | - | - | - | 2043 | - | - | - | - | 0% | 1165 | 0 | - | - | - | - | - | -23.6719 | 27.6357
base | Kathu Solar Park | aga | CSP | Generator | Existing | 100 | - | - | - | beyond 2050 | - | - | - | - | 0% | 2902 | 0 | - | - | - | - | 6 | -27.7581 | 23.0159
base | Redstone Solar Thermal Power Plant | aga | CSP | Generator | Under construction | 100 | - | - | 2024 | beyond 2050 | - | - | - | - | 0% | 2902 | 0 | - | - | - | - | 9 | -28.3095 | 23.1041
base | Aggeneys Solar | aga | solar | Generator | Existing | 40 | - | - | - | 2046 | - | - | - | - | 0% | 872 | 0 | - | - | - | - | - | -29.2202 | 18.9152
base | Boikanyo Solar | aga | solar | Generator | Existing | 55 | - | - | - | 2046 | - | - | - | - | 0% | 872 | 0 | - | - | - | - | - | -29.1151 | 23.7491
base | Bokamoso | aga | solar | Generator | Existing | 67.9 | - | - | - | 2046 | - | - | - | - | 0% | 872 | 0 | - | - | - | - | - | -26.854 | 26.6421
base | Copperton Windfarm | aga | onwind | Generator | Existing | 102 | - | - | - | 2041 | - | - | - | - | 0% | 687 | 0 | - | - | - | - | - | -29.9647 | 22.3394
base | De Wildt | aga | solar | Generator | Existing | 50 | - | - | - | 2046 | - | - | - | - | 0% | 872 | 0 | - | - | - | - | - | -25.6097 | 27.8077
base | Dyason's Klip 1 | aga | solar | Generator | Existing | 75 | - | - | - | 2046 | - | - | - | - | 0% | 872 | 0 | - | - | - | - | - | -28.4149 | 21.2219
base | Dyason's Klip 2 | aga | solar | Generator | Existing | 75 | - | - | - | 2046 | - | - | - | - | 0% | 872 | 0 | - | - | - | - | - | -28.4149 | 21.2219
base | Excelsior Wind Energy Facility | aga | onwind | Generator | Existing | 31.9 | - | - | - | 2041 | - | - | - | - | 0% | 687 | 0 | - | - | - | - | - | -34.0247 | 20.4319
base | Garob Wind Farm | aga | onwind | Generator | Existing | 135.93 | - | - | - | 2041 | - | - | - | - | 0% | 687 | 0 | - | - | - | - | - | -29.9647 | 22.3394
base | Golden Valley Wind | aga | onwind | Generator | Existing | 117.72 | - | - | - | 2041 | - | - | - | - | 0% | 687 | 0 | - | - | - | - | - | -32.7461 | 25.807
base | Kangnas Wind Farm | aga | onwind | Generator | Existing | 136.7 | - | - | - | 2041 | - | - | - | - | 0% | 687 | 0 | - | - | - | - | - | -29.6657 | 17.8878
base | Konkoonsies II Solar PV Facility | aga | solar | Generator | Existing | 75 | - | - | - | 2046 | - | - | - | - | 0% | 872 | 0 | - | - | - | - | - | -29.1621 | 19.3863
base | Kruisvallei Hydro | aga | hydro | Generator | Existing | 3.8 | - | - | - | beyond 2050 | - | - | - | - | 0% | 1240 | 0 | - | - | - | - | - | -28.2425 | 28.3077
base | Matla A Bokone Solar | aga | solar | Generator | Existing | 75 | - | - | - | 2046 | - | - | - | - | 0% | 872 | 0 | - | - | - | - | - | -28.7251 | 24.7517
base | Ngodwana Energy | aga | biomass | Generator | Existing | 25 | - | 32 | - | beyond 2050 | - | 1650 | - | - | 0% | 1500 | 0 | - | 6 | 4 |  |  | -25.4809 | 30.9743
base | Nxuba Wind Farm | aga | onwind | Generator | Existing | 138.9 | - | - | - | 2041 | - | - | - | - | 0% | 687 | 0 | - | - | - | - | - | -32.7461 | 25.807
base | Oyster Bay Wind Farm | aga | onwind | Generator | Existing | 140 | - | - | - | 2041 | - | - | - | - | 0% | 687 | 0 | - | - | - | - | - | -34.0016 | 24.7416
base | Perdekraal East Wind Farm | aga | onwind | Generator | Existing | 107.76 | - | - | - | 2041 | - | - | - | - | 0% | 687 | 0 | - | - | - | - | - | -33.3394 | 20.0293
base | Roggeveld Wind Farm | aga | onwind | Generator | Existing | 140 | - | - | - | 2041 | - | - | - | - | 0% | 687 | 0 | - | - | - | - | - | -32.4095 | 20.6698
base | Sirius Solar PV Project One | aga | solar | Generator | Existing | 75 | - | - | - | 2046 | - | - | - | - | 0% | 872 | 0 | - | - | - | - | - | -28.4149 | 21.2219
base | Soetwater Wind Farm | aga | onwind | Generator | Under construction | 139.4 | - | - | 2024 | 2042 | - | - | - | - | 0% | 687 | 0 | - | - | - | - | - | -32.4095 | 20.6698
base | Solar Capital Orange | aga | solar | Generator | Under construction | 75 | - | - | 2023 | 2047 | - | - | - | - | 0% | 872 | 0 | - | - | - | - | - | -30.9181 | 19.441
base | The Karusa Wind Farm | aga | onwind | Generator | Existing | 139.8 | - | - | - | 2046 | - | - | - | - | 0% | 687 | 0 | - | - | - | - | - | -32.4095 | 20.6698
base | Waterloo Solar Park | aga | solar | Generator | Existing | 75 | - | - | - | 2046 | - | - | - | - | 0% | 872 | 0 | - | - | - | - | - | -26.9382 | 24.7049
base | Wesley Ciskei | aga | onwind | Generator | Existing | 32.7 | - | - | - | 2041 | - | - | - | - | 0% | 687 | 0 | - | - | - | - | - | -33.2824 | 27.4298
base | Zeerust | aga | solar | Generator | Existing | 75 | - | - | - | 2046 | - | - | - | - | 0% | 872 | 0 | - | - | - | - | - | -25.2366 | 26.0824
base | Kelvin | aga | coal | Generator | Existing | 160 | - | - | - | 2027 | 12.372 | 15.6 | 0.5 | 0.5 | 30% | 80 | 0 | - | - | - | - | - | -26.658 | 28.1138
base | Sasol SSF | aga | coal | Generator | Existing | 600 | - | - | - | beyond 2050 | 12.372 | 15.6 | 0.5 | 0.5 | 0% | 900 | 0 | - | - | - | - | - | -26.5036 | 29.1803
base | Avon | aga | gas | Generator | Existing | 670 | 167.5 | 4 | - | 2046 | 11.519 | 263.4 | 11 | 11 | 0% | 3 | 169 | - | - | - | - | - | -29.251 | 31.0941
base | Dedisa | aga | gas | Generator | Existing | 335 | 167.5 | 2 | - | 2046 | 11.519 | 263.4 | 11 | 11 | 0% | 3 | 169 | - | - | - | - | - | -33.4433 | 25.4022
base | Sasol Infrach Engines | aga | gas | Generator | Existing | 175 | 9.7 | 18 | - | beyond 2050 | 7.6 | 75 | 8 | 8 | 30% | 950 | 0 | - | - | - | - | - | -26.8102 | 27.8277
base | Sasol OCGT | aga | gas | Generator | Existing | 250 | 50 | 5 | - | beyond 2050 | 11.519 | 75 | 2 | 2 | 0% | 950 | 0 | - | - | - | - | - | -26.8102 | 27.8277
base | CahoraBassa | aga | hydro-import | Generator | Existing | 1764 | 250 | 6 | - | beyond 2050 | - | - | - | - | 0% | 300 | 0 | - | - | - | - | -
base | ColleyWobbles | aga | hydro | Generator | Existing | 65 | 65 | 1 | - | beyond 2050 | - | - | - | - | 0% | 300 | 0 | - | - | - | - | - | -32.05 | 28.5833
base | Mondi | aga | biomass | Generator | Existing | 120 | 30 | 4 | - | beyond 2050 | - | - | 0.5 | 0.5 | 30% | 500 | 0 | - | - | - | - | -
base | Sappi | aga | biomass | Generator | Existing | 144 | 36 | 4 | - | beyond 2050 | - | - | 0.5 | 0.5 | 30% | 500 | 0 | - | - | - | - | - | -25.3447 | 30.394
base | Steenbras | aga | PHS | StorageUnit | Existing | 180 | 45 | 4 | - | beyond 2050 | - | - | - | - | 0% | 300 | 222 | 72% | 4 | 45 | 2.7 | - | -34.153 | 18.9

## new_build_limits
scenario | parameter | carrier (MW) | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050
base | max_installed_limit | solar | 2019: 0; 2020: 0; 2021: 0
base | max_installed_limit | onwind | 2019: 0; 2020: 0; 2021: 0
base | max_installed_limit | CCGT | 2019: 0; 2020: 0; 2021: 0
base | max_installed_limit | OCGT | 2019: 0; 2020: 0; 2021: 0
base | max_installed_limit | biomass | 2019: 0; 2020: 0; 2021: 0
base | max_installed_limit | coal | 2019: 0; 2020: 0; 2021: 0
base | max_installed_limit | nuclear | 2019: 0; 2020: 0; 2021: 0; 2022: 0; 2023: 0; 2024: 0; 2025: 0; 2026: 0
base | max_installed_limit | hydro-import | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
base | max_installed_limit | PHS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000
base | max_installed_limit | battery | 2019: 0; 2020: 0; 2021: 0
base | min_installed_limit | solar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
base | min_installed_limit | onwind | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
base | min_installed_limit | CCGT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
base | min_installed_limit | OCGT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
base | min_installed_limit | coal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
base | min_installed_limit | nuclear | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
base | min_installed_limit | hydro-import | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
base | min_installed_limit | PHS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
base | min_installed_limit | battery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ambitions_LC_SMOOTH | max_installed_limit | solar | 2019: 0
ambitions_LC_SMOOTH | max_installed_limit | onwind | 2019: 0
ambitions_LC_SMOOTH | max_installed_limit | CCGT | 2019: 0
ambitions_LC_SMOOTH | max_installed_limit | OCGT | 2019: 0
ambitions_LC_SMOOTH | max_installed_limit | biomass | 2019: 0
ambitions_LC_SMOOTH | max_installed_limit | coal | 2019: 0
ambitions_LC_SMOOTH | max_installed_limit | nuclear | 2019: 0; 2020: 0; 2021: 0; 2022: 0; 2023: 0; 2024: 0; 2025: 0; 2026: 0
ambitions_LC_SMOOTH | max_installed_limit | hydro-import | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ambitions_LC_SMOOTH | max_installed_limit | PHS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000
ambitions_LC_SMOOTH | max_installed_limit | battery | 2019: 0
ambitions_LC_SMOOTH | min_installed_limit | solar | 0 | 0 | 0 | 4000 | 5500 | 7400 | 9800 | 12700 | 16100 | 19500 | 22900 | 26300 | 29200 | 31600 | 33500 | 34900 | 36300 | 37700 | 39100 | 40500 | 41900 | 43300 | 44700 | 46100 | 47500 | 48900 | 50300 | 51700 | 52600 | 53500 | 54400 | 55300
ambitions_LC_SMOOTH | min_installed_limit | onwind | 0 | 0 | 0 | 1600 | 3200 | 4800 | 6400 | 8000 | 9600 | 11200 | 12800 | 14700 | 16900 | 19400 | 22200 | 25400 | 28600 | 31800 | 35000 | 38200 | 41400 | 44600 | 47800 | 49400 | 51000 | 52600 | 54200 | 55800 | 57400 | 59000 | 60600 | 62200
ambitions_LC_SMOOTH | min_installed_limit | CCGT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ambitions_LC_SMOOTH | min_installed_limit | OCGT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ambitions_LC_SMOOTH | min_installed_limit | coal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ambitions_LC_SMOOTH | min_installed_limit | nuclear | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ambitions_LC_SMOOTH | min_installed_limit | hydro-import | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ambitions_LC_SMOOTH | min_installed_limit | PHS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ambitions_LC_SMOOTH | min_installed_limit | battery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ambitions_2Gt_SMOOTH | max_installed_limit | solar | 2019: 0
ambitions_2Gt_SMOOTH | max_installed_limit | onwind | 2019: 0
ambitions_2Gt_SMOOTH | max_installed_limit | CCGT | 2019: 0
ambitions_2Gt_SMOOTH | max_installed_limit | OCGT | 2019: 0
ambitions_2Gt_SMOOTH | max_installed_limit | biomass | 2019: 0
ambitions_2Gt_SMOOTH | max_installed_limit | coal | 2019: 0
ambitions_2Gt_SMOOTH | max_installed_limit | nuclear | 2019: 0; 2020: 0; 2021: 0; 2022: 0; 2023: 0; 2024: 0; 2025: 0; 2026: 0
ambitions_2Gt_SMOOTH | max_installed_limit | hydro-import | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ambitions_2Gt_SMOOTH | max_installed_limit | PHS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000
ambitions_2Gt_SMOOTH | max_installed_limit | battery | 2019: 0
ambitions_2Gt_SMOOTH | min_installed_limit | solar | 0 | 0 | 0 | 1000 | 2500 | 5000 | 8500 | 12500 | 16500 | 20500 | 24500 | 28500 | 32000 | 35000 | 37500 | 39500 | 41000 | 42500 | 44000 | 45500 | 47000 | 48500 | 50000 | 51500 | 53000 | 54500 | 56000 | 57500 | 59000 | 60500 | 62000 | 63500
ambitions_2Gt_SMOOTH | min_installed_limit | onwind | 0 | 0 | 0 | 1600 | 3400 | 5400 | 7400 | 9400 | 11400 | 13400 | 15400 | 17800 | 20600 | 23900 | 27700 | 31500 | 35300 | 39100 | 42900 | 46700 | 50500 | 54300 | 58100 | 61900 | 65700 | 69500 | 73300 | 77100 | 80900 | 84700 | 88500 | 92300
ambitions_2Gt_SMOOTH | min_installed_limit | CCGT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ambitions_2Gt_SMOOTH | min_installed_limit | OCGT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ambitions_2Gt_SMOOTH | min_installed_limit | coal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ambitions_2Gt_SMOOTH | min_installed_limit | nuclear | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ambitions_2Gt_SMOOTH | min_installed_limit | hydro-import | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ambitions_2Gt_SMOOTH | min_installed_limit | PHS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ambitions_2Gt_SMOOTH | min_installed_limit | battery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## projected_parameters
scenario | parameter | unit | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050
ambitions | annual_demand | TWh/yr | 239.5811 | 240.3108 | 241.6172 | 245.5365 | 249.7823 | 254.0281 | 257.1553 | 261.3248 | 265.4943 | 268.6214 | 272.2698 | 276.9605 | 279.5665 | 283.7359 | 286.8632 | 291.0326 | 294.1598 | 297.8081 | 301.4564 | 304.5836 | 307.7108 | 311.3591 | 314.4862 | 318.6557 | 321.2617 | 324.91 | 328.5584 | 332.2067 | 335.3338 | 338.9822 | 342.1093 | 345.7576
ambitions | coal_fleet_EAF | %/yr | 58.54% | 57.31% | 56.53% | 56.36% | 56.41% | 55.76% | 55.63% | 55.78% | 55.64% | 55.67% | 56.34% | 57.18% | 57.51% | 58.2% | 58.87% | 59.38% | 59.58% | 60.27% | 61.28% | 61.82% | 61.87% | 62.39% | 65.32% | 65.71% | 66.29% | 66.6% | 67.11% | 67.49% | 68.43% | 69.59% | 71.02% | 71.84%
ambitions | spinning_reserves | MW | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800
ambitions | total_reserves | MW | 2200 | 2200 | 2200 | 2200 | 2200 | 2200 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400
ambitions | reserve_margin_active | TRUE/FALSE | 0 | 0 | 0 | 0 | 1 | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
ambitions | reserve_margin | % | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10%
Note on D2: Peter Klein Excludes pumping Demand increased 1/0.98 for Sasol generation which is not accounted for by Eskom

## costs
scenario | technology | parameter | 2019 | 2020 | 2025 | 2030 | 2035 | 2040 | 2045 | 2050 | unit | source
ambitions_2019 | coal | CO2 intensity | 0.3 | 0.3 | 0.3 | 0.29 | 0.3 | 0.325 | 0.325 | 0.325 | tCO2/MWth | https://www.eia.gov/environment/emissions/co2_vol_mass.php
ambitions_2019 | CSP | CO2 intensity | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | tCO2/MWth | https://www.eia.gov/environment/emissions/co2_vol_mass.php
ambitions_2019 | diesel | CO2 intensity | 0.248 | 0.248 | 0.248 | 0.248 | 0.248 | 0.248 | 0.248 | 0.248 | tCO2/MWth | https://www.eia.gov/environment/emissions/co2_vol_mass.php
ambitions_2019 | gas | CO2 intensity | 0.1794 | 0.1794 | 0.1794 | 0.1794 | 0.1794 | 0.1794 | 0.1794 | 0.1794 | tCO2/MWth | https://www.eia.gov/environment/emissions/co2_vol_mass.php
ambitions_2019 | solar | discount rate | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | per unit
ambitions_2019 | solar-rooftop | discount rate | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | per unit
ambitions_2019 | solar-utility | discount rate | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | 8.2% | per unit
ambitions_2019 | biomass | heat_rate | 12.386 | 12.386 | 12.386 | 12.386 | 12.386 | 12.386 | 12.386 | 12.386 | GJ/MWh
ambitions_2019 | CCGT | heat_rate | 7.395 | 7.395 | 7.395 | 7.395 | 7.395 | 7.395 | 7.395 | 7.395 | GJ/MWh
ambitions_2019 | coal | heat_rate | 9.812 | 9.812 | 9.812 | 9.812 | 9.812 | 9.812 | 9.812 | 9.812 | GJ/MWh
ambitions_2019 | CSP | heat_rate | [8 empty] | GJ/MWh
ambitions_2019 | diesel | heat_rate | 11.519 | 11.519 | 11.519 | 11.519 | 11.519 | 11.519 | 11.519 | 11.519 | GJ/MWh
ambitions_2019 | nuclear | heat_rate | 10.657 | 10.657 | 10.657 | 10.657 | 10.657 | 10.657 | 10.657 | 10.657 | GJ/MWh
ambitions_2019 | OCGT | heat_rate | 11.519 | 11.519 | 11.519 | 11.519 | 11.519 | 11.519 | 11.519 | 11.519 | GJ/MWh
ambitions_2019 | battery inverter | efficiency | 89% | 89% | 89% | 89% | 89% | 89% | 89% | 89% | per unit
ambitions_2019 | biomass | efficiency | 29.07% | 29.07% | 29.07% | 29.07% | 29.07% | 29.07% | 29.07% | 29.07% | per unit
ambitions_2019 | CCGT | efficiency | 48.68% | 48.68% | 48.68% | 48.68% | 48.68% | 48.68% | 48.68% | 48.68% | per unit
ambitions_2019 | coal | efficiency | 36.69% | 36.69% | 36.69% | 36.69% | 36.69% | 36.69% | 36.69% | 36.69% | per unit
ambitions_2019 | CSP | efficiency | [8 empty] | per unit
ambitions_2019 | diesel | efficiency | 31.25% | 31.25% | 31.25% | 31.25% | 31.25% | 31.25% | 31.25% | 31.25% | per unit
ambitions_2019 | nuclear | efficiency | 33.78% | 33.78% | 33.78% | 33.78% | 33.78% | 33.78% | 33.78% | 33.78% | per unit
ambitions_2019 | OCGT | efficiency | 31.25% | 31.25% | 31.25% | 31.25% | 31.25% | 31.25% | 31.25% | 31.25% | per unit
ambitions_2019 | onwind | efficiency | [8 empty] | per unit
ambitions_2019 | PHS | efficiency | 75% | 75% | 75% | 75% | 75% | 75% | 75% | 75% | per unit
ambitions_2019 | hydro | efficiency | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90% | per unit
ambitions_2019 | hydro-import | efficiency | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90% | per unit
ambitions_2019 | solar | efficiency | [8 empty] | per unit
ambitions_2019 | solar-rooftop | efficiency | [8 empty] | per unit
ambitions_2019 | solar-utility | efficiency | [8 empty] | per unit
ambitions_2019 | battery inverter | FOM | 697 | 697 | 697 | 697 | 697 | 697 | 697 | 697 | ZAR/kWel
ambitions_2019 | biomass | FOM | 2028 | 2028 | 2028 | 2028 | 2028 | 2028 | 2028 | 2028 | ZAR/kWel
ambitions_2019 | CCGT | FOM | 203 | 203 | 203 | 203 | 203 | 203 | 203 | 203 | ZAR/kWel
ambitions_2019 | coal | FOM | 1133 | 1133 | 1133 | 1133 | 1133 | 1133 | 1133 | 1133 | ZAR/kWel
ambitions_2019 | CSP | FOM | 1203 | 1203 | 1203 | 1203 | 1203 | 1203 | 1203 | 1203 | %/year
ambitions_2019 | diesel | FOM | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | %/year
ambitions_2019 | HVAC overhead | FOM | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | %/year
ambitions_2019 | HVDC inverter pair | FOM | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | %/year
ambitions_2019 | HVDC overhead | FOM | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | %/year
ambitions_2019 | HVDC submarine | FOM | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | %/year
ambitions_2019 | nuclear | FOM | 1187 | 1187 | 1187 | 1187 | 1187 | 1187 | 1187 | 1187 | ZAR/kWel
ambitions_2019 | OCGT | FOM | 196 | 196 | 196 | 196 | 196 | 196 | 196 | 196 | ZAR/kWel
ambitions_2019 | onwind | FOM | 742 | 742 | 742 | 742 | 742 | 742 | 742 | 742 | ZAR/kWel
ambitions_2019 | PHS | FOM | 222 | 222 | 222 | 222 | 222 | 222 | 222 | 222 | ZAR/kWel
ambitions_2019 | hydro | FOM | 484 | 484 | 484 | 484 | 484 | 484 | 484 | 484 | ZAR/kWel
ambitions_2019 | hydro-import | FOM | 484 | 484 | 484 | 484 | 484 | 484 | 484 | 484 | ZAR/kWel
ambitions_2019 | solar | FOM | 328 | 328 | 328 | 328 | 328 | 328 | 328 | 328 | ZAR/kWel
ambitions_2019 | solar-rooftop | FOM | 328 | 328 | 328 | 328 | 328 | 328 | 328 | 328 | ZAR/kWel
ambitions_2019 | solar-utility | FOM | 328 | 328 | 328 | 328 | 328 | 328 | 328 | 328 | ZAR/kWel
ambitions_2019 | biomass | fuel | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | R/GJ
ambitions_2019 | coal | fuel | 33.8 | 33.8 | 33.8 | 33.8 | 33.8 | 33.8 | 33.8 | 33.8 | R/GJ
ambitions_2019 | CSP | fuel | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | R/GJ
ambitions_2019 | diesel | fuel | 277.8 | 277.8 | 277.8 | 277.8 | 277.8 | 277.8 | 277.8 | 277.8 | R/GJ
ambitions_2019 | gas | fuel | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | R/GJ
ambitions_2019 | nuclear | fuel | 9.1 | 9.1 | 9.1 | 9.1 | 9.1 | 9.1 | 9.1 | 9.1 | R/GJ
ambitions_2019 | uranium | fuel | [8 empty] | R/GJ
ambitions_2019 | battery inverter | investment | 12286.0339 | 11397.0796 | 8587.8391 | 7192.4046 | 6742.8794 | 6293.3541 | 5843.8288 | 5394.3035 | ZAR/kWel
ambitions_2019 | battery storage | investment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ZAR/kWh
ambitions_2019 | biomass | investment | 52707.7547 | 52707.7547 | 52707.7547 | 52707.7547 | 52707.7547 | 52707.7547 | 52707.7547 | 52707.7547 | ZAR/kWel
ambitions_2019 | CCGT | investment | 12198.9349 | 12198.9349 | 12198.9349 | 12198.9349 | 12198.9349 | 12198.9349 | 12198.9349 | 12198.9349 | ZAR/kWel
ambitions_2019 | coal | investment | 48188.4161 | 48188.4161 | 48188.4161 | 48188.4161 | 48188.4161 | 48188.4161 | 48188.4161 | 48188.4161 | ZAR/kWel
ambitions_2019 | CSP | investment | 126012.6516 | 120571.6629 | 98228.2623 | 83707.865 | 74928.1707 | 70234.0768 | 67921.8009 | 66343.1945 | ZAR/kWel
ambitions_2019 | diesel | investment | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | ZAR/kWel
ambitions_2019 | HVAC overhead | investment | 6000 | 6000 | 6000 | 6000 | 6000 | 6000 | 6000 | 6000 | ZAR/MW/km
ambitions_2019 | HVDC inverter pair | investment | [8 empty] | ZAR/MW
ambitions_2019 | HVDC overhead | investment | 6000 | 6000 | 6000 | 6000 | 6000 | 6000 | 6000 | 6000 | ZAR/MW/km
ambitions_2019 | HVDC submarine | investment | [8 empty] | ZAR/MW/km
ambitions_2019 | nuclear | investment | 94145.259 | 93963.8616 | 93056.8745 | 92149.8874 | 91968.49 | 91968.49 | 91968.49 | 91968.49 | ZAR/kWel
ambitions_2019 | OCGT | investment | 10753.7889 | 10753.7889 | 10753.7889 | 10753.7889 | 10753.7889 | 10753.7889 | 10753.7889 | 10753.7889 | ZAR/kWel
ambitions_2019 | onwind | investment | 14691 | 14431 | 13131 | 11831 | 11190 | 10544 | 9893 | 9238 | ZAR/kWel
ambitions_2019 | PHS | investment | 30777.1918 | 30777.1918 | 30777.1918 | 30777.1918 | 30777.1918 | 30777.1918 | 30777.1918 | 30777.1918 | ZAR/kWel
ambitions_2019 | hydro | investment | 74339.708 | 74339.708 | 74339.708 | 74339.708 | 74339.708 | 74339.708 | 74339.708 | 74339.708 | ZAR/kWel
ambitions_2019 | hydro-import | investment | 74339.708 | 74339.708 | 74339.708 | 74339.708 | 74339.708 | 74339.708 | 74339.708 | 74339.708 | ZAR/kWel
ambitions_2019 | solar | investment | 8746 | 8206 | 6671 | 5136 | 4402 | 3844 | 3506 | 3238 | ZAR/kWel
ambitions_2019 | solar-rooftop | investment | 8746 | 8206 | 6671 | 5136 | 4402 | 3844 | 3506 | 3238 | ZAR/kWel
ambitions_2019 | solar-utility | investment | 8746 | 8206 | 6671 | 5136 | 4402 | 3844 | 3506 | 3238 | ZAR/kWel
ambitions_2019 | battery inverter | lifetime | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | years
ambitions_2019 | battery storage | lifetime | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | years
ambitions_2019 | biomass | lifetime | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | years
ambitions_2019 | CCGT | lifetime | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | years
ambitions_2019 | coal | lifetime | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | years
ambitions_2019 | CSP | lifetime | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | years
ambitions_2019 | diesel | lifetime | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | years
ambitions_2019 | HVAC overhead | lifetime | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | years
ambitions_2019 | HVDC inverter pair | lifetime | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | years
ambitions_2019 | HVDC overhead | lifetime | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | years
ambitions_2019 | HVDC submarine | lifetime | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | years
ambitions_2019 | hydro | lifetime | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | years
ambitions_2019 | hydro-import | lifetime | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | years
ambitions_2019 | nuclear | lifetime | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | years
ambitions_2019 | OCGT | lifetime | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | years
ambitions_2019 | onwind | lifetime | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | years
ambitions_2019 | PHS | lifetime | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | years
ambitions_2019 | ror | lifetime | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | years
ambitions_2019 | solar | lifetime | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | years
ambitions_2019 | solar-rooftop | lifetime | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | years
ambitions_2019 | solar-utility | lifetime | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | years
ambitions_2019 | CCGT | VOM | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | ZAR/MWhel
ambitions_2019 | coal | VOM | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | ZAR/MWhel
ambitions_2019 | CSP | VOM | [8 empty] | ZAR/MWhel | bar: 2019 to 2050
ambitions_2019 | diesel | VOM | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | EUR/MWhel
ambitions_2019 | nuclear | VOM | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | ZAR/MWhel
ambitions_2019 | OCGT | VOM | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | ZAR/MWhel
ambitions_2019 | onwind | VOM | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | ZAR/MWhel
ambitions_2019 | solar | VOM | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ZAR/MWhel

## carriers
scenario | carrier | parameter |  | unit | source
ambitions_2019 | coal | CO2 intensity | 0.3 | tCO2/MWth | https://www.eia.gov/environment/emissions/co2_vol_mass.php
ambitions_2019 | CSP | CO2 intensity | 0 | tCO2/MWth | https://www.eia.gov/environment/emissions/co2_vol_mass.php
ambitions_2019 | diesel | CO2 intensity | 0.248 | tCO2/MWth | https://www.eia.gov/environment/emissions/co2_vol_mass.php
ambitions_2019 | gas | CO2 intensity | 0.1794 | tCO2/MWth | https://www.eia.gov/environment/emissions/co2_vol_mass.php